R.STAHL offers a customer specific factory set-up for the ISpac isolator.

This form can be downloaded from the internet applying the webcode „9182A“.You may find the document under: “Downloads – data sheets“. Please edit the form directly on your PC and pass it along with your order to your R. STAHL representative.

# AB-no.:	        - Pos.:      	Volume:

type			channels		output		limit value / set point	functional safety

9182 / 10 - 51 - 11.		1		0/4...20 mA	without

9182 / 10 - 51 - 13.		1		0/4...20 mA	without			SIL 2

9182 / 10 - 51 - 12.		1		0/4...20 mA	2 NO

9182 / 10 - 51 - 14.		1		0/4...20 mA	2 NO			SIL 2

9182 / 20 - 51 - 11.		2		0/4...20 mA	without

9182 / 20 - 50 - 12.		2		without		2 NO per channel

Non-Ex i / Non I.S.:

9182 / 10 - 51 - 64.		1		0/4...20 mA	2 NO			SIL 2

Equipped with:	 Screw terminals s 	 Spring terminals k

Please read the operating instructions before you start to fill in the following form. Please tick only one selection per parameter and channel.

|  | factory default: | channel 1 |  |  | ###### channel 2 |
| --- | --- | --- | --- | --- | --- |
| ###### Signal-TAG | serial number |  |  |  |  |
| Ex i Input |  |  |  |  |  |
| RTD |  |  |  |  |  |
| sensor type | PT 100 |  | PT 100 PT 250 PT 500 PT 1000 PT 2000 NI 100 NI 500 NI 1000 PT 100 GOST, M50 GOST, M100 GOST, CU53 GOST | PT 100 PT 250 PT 500 PT 1000 PT 2000 NI 100 NI 500 NI 1000 PT 100 GOST, M50 GOST, M100 GOST, CU53 GOST |  |
| connection type | 3-wire |  | 2-wire 3-wire 4-wire | 2-wire 3-wire 4-wire |  |
| measurement range | 0 °C ... 400 °C |  | from till °C °F K Ω | from till °C °F K Ω |  |
| Thermo couple |  |  |  |  |  |
| sensor type |  |  | type B type E type J type K type N type R type S type T typ L type U type XK | type B type E type J type K type N type R type S type T typ L type U type XK |  |
| CJC type |  |  | external PT 100 fixed Temp. | external PT 100 fixed Temp. |  |
| measurement range |  |  | from till °C °F K mV | from till °C °F K mV |  |
| Resistance transmitter / potentiometer |  |  |  |  |  |
| sensor type |  |  | 50 … 500 Ω 0,5 … 5 kΩ 1 … 10 kΩ 10 … 100 kΩ (+ Shunt) | 50 … 500 Ω 0,5 … 5 kΩ 1 … 10 kΩ 10 … 100 kΩ (+ Shunt) |  |
| measurement range |  |  | from % till % | from % till % |  |
| Output (only 9182/*0-51-1*) |  |  |  |  |  |
| signal | 4 mA ... 20 mA | 0 mA ... 20 mA 4 mA ... 20 mA |  | 0 mA ... 20 mA 4 mA ... 20 mA |  |
| fault behaviour | output fault value : 2,4 mA | Output fault value: Hold last value fault detection off |  | Output fault value: Hold last value fault detection off |  |
| Limit value A (9182/*0-5*-12. and 9182 / 10 - 51 - *4.) |  |  |  |  |  |
| Behaviour contact | inactive | inactive closed if value > limit value *) closed if value < limit value *) open, if value > limit value open, if value < limit value |  | inactive closed if value > limit value *) closed if value < limit value *) open, if value > limit value open, if value < limit value |  |
| Limit value | 25 % | % (0…100 %, take hysteresis into account) |  | % (0…100 %, take hysteresis into account) |  |
| Hysteresis | 1 % | % (0,1 % ... 10 %) |  | % (0,1 % ... 10 %) |  |
| Reset lockout | deactivated | activated deactivated active-pwrrst |  | activated deactivated active-pwrrst |  |
| Limit value B (9182/*0-5*-12. and 9182 / 10 - 51 - *4.) |  |  |  |  |  |
| Behaviour contact | inactive | inactive closed if value > limit value *) closed if value < limit value *) open, if value > limit value open, if value < limit value |  | inactive closed if value > limit value *) closed if value < limit value *) open, if value > limit value open, if value < limit value |  |
| Limit value | 25 % | % (0…100 %, take hysteresis into account) |  | % (0…100 %, take hysteresis into account) |  |
| Hysteresis | 1 % | % (0,1 % ... 10 %) |  | % (0,1 % ... 10 %) |  |
| Reset lockout | deactivated | activated deactivated active-pwrrst |  | activated deactivated active-pwrrst |  |

*) Not available for 9182/10 - 51 - 14.